## Influent Measurements
Date	#/type	Ammonium [mg/L]	Ortho Phosphate [mg/L]	COD	BOD	T	Conductivity [mS/cm]	pH	Nitrate total [mg/L]	Nitrite	Turbidity [ntu]
13-9-2024	Start BE
23-9-2024	1	>6						7,21	25	3	61,8
	2	>6						7,24	25	3	89,5
	3	>6						7,25	25	3	93,9
	kit	54,3	11,9		2175
30-9-2024	1	148	35,8		9375		1,774	8,74	263		135
	2	164	36,4				1,809	8,73	252		165
	3	179	33,1				1,815	8,73	319		157
7-10-2024	1	551	69,6		546		2,52	8,11	299		330
	2	552	68,4		1329		2,43	8,11	300		345
	3	553	67		dilution f. uit!			8,11	22,4		350
14-10-2024	1	22,9	54	690			2,07	8,82			281
	2	20,7	52,6				2,02	8,81			266
	3	21,9	54				2,02	8,8			262
21-10-2024	1	niet meetbaar	69,3	1758			2,19	7,46
	2		131	1483			2,17	7,47
	3		65,1				2,26	7,48
18-11-2024	1	292	18	354	17		1,309	7,96	139 (above range)		117
	2	248	17,7	315	0		1,288	7,88	139		97,5
	3	282	17,8	379			1,307	7,87	140		90,7
27-11-2024	1	74,4	9,54		45				81,7		50,5
	2	70,7	9,62						80,8		52
	3	135,3							80,4		53,2
2-12-2024	1	2,76	21,2		63		1,356	8,29	125		118
	2	2,64	21,2		10		1,353	8,27	126		112
	3	2,92	20,2				1,35	8,27			123
9-12-2024		113	37,7				1,528	8,27	190		219
		106	37,5				1,535	8,25	188		209
											214

## Effluent Measurements
Date	#/type	Ammonium [mg/L]	Ortho Phosphate [mg/L]	COD	BOD	T	Conductivity [µS/cm]	pH	Nitrate total [mg/L]	Nitrite	Turbidity [ntu]
13-9-2024	Start BE
23-9-2024	1	2						8,05	>500	>80	0,14
	2	2						8,05	>500	>80	1,22
	3	2						8,06	>500	>80	0,56
	kit	0,579	2,44		0
30-9-2024	1	2	13,8		0		1,03	7,16	108		0,14
	2	3	13,9				1,045	7,18	93,2		0,2
	3	4	13,9				1,045	7,2	91,9		0,15
7-10-2024	1	8,24	24,4		9		1,785	7,37	162		0,04
	2	9,47	24,5		dilution f. uit!		1,789	7,4	158		0,39
	3	9,9	24,5				1,771	7,4	163		0,08
14-10-2024	1	20	19,2	62,2			1,105	6,36			0,56
	2	20	19,2				1,093	6,35			0,78
	3	20	19,2				1,092	6,36			0,44
21-10-2024	1	niet meetbaar	23	137			1,612	7,93
	2		23,2				1,708	7,94
	3		23,1				1,63	7,92
18-11-2024	1	1,1	2,31	24,9	1		1,007	7,65	17,4 (underneath range)		0,39
	2	1,17	2,44	11,6	0		1,011	7,69	19,2		0,34
	3	1,07	2,29	22			1,017	7,71	19,6		0,45
25-11-2024	1	0,144	1,92
	2	0,152	1,88
	3	0,129	1,91
27-11-2024	1	1,67	1,86		0				10,6		0,33
	2	1,71	2,01		0				11,7		0,25
									9,82		0,08
2-12-2024	1	110	1,41		0		1,077	7,65	15,6		0,02
	2	90,8	1,36		0		1,092	7,7	15,6		0,06
	3	85,70	1,31				1,098	7,68			0,02
9-12-2024		20,6	1,69				1,055	7,8	19,2		0
		20,7	1,74				1,047	7,85	19		0,03
											0,13

## Sludge Measurements
Date	#/type	Ammonium [mg/L]	Ortho Phosphate [mg/L]	COD	BOD	T	Conductivity [µS/cm]	pH	Nitrate total [mg/L]	Nitrite	Turbidity [ntu]
13-9-2024	Start BE
23-9-2024	1	2						7,62	>500	>80	604
	2	2						7,62	>500	>80	609
	3	2						7,64	>500	>80	593
	kit	1,77	55,7		14700
30-9-2024	1	4	-		40050		1,022	6,86	201		653
	2	4	-				1,02	6,94	241		656
	3	4	-				1,036	6,92	-		641
7-10-2024	1	11,3	89,8		1227		1,745	7,2	242		650
	2	6,97	109		dilution f. uit!		1,742	7,19	288		631
	3	9,8	120				1,726	7,19	241		619
14-10-2024	1	20,5	142	1277(above range)			1,036	6,98			270
	2	20,5					1,015	6,94			255
	3	20,3					1,006	6,92			278
21-10-2024	1		onstabiele lichtomstandigheden	1577			1,491	7,38
	2			1634			1,493	7,37
	3						1,462	7,38
18-11-2024	1	0,036 (under measuring value)	onstabiele lichtomstandigheden	4029	242		0,997	7,16	233		419
	2	1,5		3449	311		1,009	7,24	226		423
	3	1,66		3152			1,008	7,26	229		369
27-11-2024	1	1,73	119		245				10,3		345
	2	1,85	116		219				10,9		330
	3								11		337
2-12-2024	1	158	116		86		1,082	7,16	141		750
	2	159	89,6		245		1,082	7,1	144		707
	3	168	104				1,093	7,12			754
9-12-2024		8,89	18,3				1,092	7,28	145		33,2
		8,97	36				1,089	7,24	147		35,4
											32,7

## Benodigdheden
				Daphne’s gedachten
				PH – KCL
				PH kalibratie 80%

Small markers
Medium gloves

## Test kits
	Influent	Effluent	Sludge	Note				# repeats
Ammonium	LCK502	LCK305	LCK305					3
Orth phosphate	LCK049	LCK049	LCK049
COD	LCI400	LCI400	LCI400	+1 calibration for each time measuring
BOD	LCK555	LCK555	LCK555
T
Conductivity
pH
Total nitrogen	LCK338	LCK338	LCK338
Turbidity

	#samples for kit	#week	#repeats	#stock	#extra	#required	#order cuvettes
LCK502	1	17	3	49	0	51	2
LCK305	2	17	3	0	0	102	102
LCK049	3	17	3	47	0	153	106
LCI400	3	17	3	0	1	170	170
LCK555	3	17	3	>153	0	153	0	all past due date
LCK338	3	17	3	50	0	153	103